## Sheet2
Special requirements for Specific Hazard Categories
| For all compressed gases | FLAMMABLE/COMBUSTIBLE | REACTIVE | OXIDIZER | CORROSIVE | TOXIC | ASPHYXIANT | PYROPHORIC | CRYOGENICS
Definition | Disclaimer: If the compressed gas in question has multiple hazards, please look into each hazard category tand use the most conservative information. Note: Please consult your Compressed gas supplier /vendor and read the Safety Data Sheet (SDS) for the compressed gas in question, prior to its use. | PYROPHORIC: A+C3:J3 material which is a gas at one atmosphere (101.3 kPa) and 20°C, and can ignite spontaneously on contact with air at or below a temperature of 54°C. | REACTIVE : A potentialy unstable material which may in the presence of air, water, temperature changes, shock friction, static discharge or contamination release very large or potentially harmful amounts of energy. | OXIDIZING GAS: A gas that can support and accelerate the combustion of another material per NFPA. It is also defined material which is a gas at one atmosphere (101.3 kPa) and 20°C, and readily reacts to yield oxygen or other oxidizing agents to promote or cause the ignition of combustible materials. Additionally, per USDOT it includes pure gases or gas mixtures with an oxidizing power >23.5% per the CGA Handbook of Compressed Gases. | CORROSIVE GAS :A gas that causes full thickness destruction of human skin at the site of contact within a specified period of time and during transportation has exhibits a severe corrosion rate of aluminum or steel based on criteria specified in 49 CFR 173.137(c)(2). | TOXIC GAS: A gas which has a median lethal dose (LC50) of more than 200 parts per million, but not more than 2,000 parts per million when administered by continuous inhalation for 1 hour to albino rats weighing between 200 to 300 grams each per FDNY NYC Fire Code Section 3702.1. | ASPHYXIANT: A substance or mixture that displaces oxygen in the ambient atmosphere, and can thus cause oxygen deprivation in those who are exposed, leading to unconsciousness and death. | PYROPHORIC: A material which is a gas at one atmosphere (101.3 kPa) and 20°C, and can ignite spontaneously on contact with air at or below a temperature of 54°C. | CRYOGENIC: A fluid having a boiling point lower than -130oF (-89.9oC) at 14.7 pounds per square inch absolute (psia) (an absolute pressure of 101.3 kPa) per FDNY NYC Fire Code Section FC3202.1
Examples of Specific Gases |  | Methane, Ethane, Propane, Butane, Hydrogen, Acetylene, Arsine, Phosphine, Dichlorosilane | Chlorine, Fluorine, Hydrogen fluoride, Hydrogen chloride, Sulfur dioxide | Oxygen, Chlorine | Hydrogen fluoride, Hydrogen chloride, Sulfur dioxide, Boron Trichloride, Dichlorosilane , Ammonia | Arsine, Chlorine, Fluorine, Hydrogen fluoride, Hydrogen chloride, Sulfur dioxide, Carbon monoxide, Phosphine, Phosgene, Hydrogen sulfide, Nitric oxide, Ethylene oxide, Boron Trichloride, Dichlorosilane | Carbon dioxide,Carbon monoxide, Nitrogen, Sulfur hexafluoride, Noble gases (Helium, Neon, Krypton, Xenon), Octofluorocyclobutane | Silane, Disilane, Trimethyl boron | Helium, Liquid Nitrogen, Liquid Argon, Carbon dioxide and Nitrous oxide,
Labelling and Signage | • Hazard identification signs as set forth in NFPA 704 (NFPA Diamonds) for the specific material contained must be conspicuously affixed on stationary containers and at the entrances to locations where hazardous material are stored, handled or used. (2703.5). Individual containers shall be conspicuously marked or labeled. Signs reading " COMPRESSED GAS" shall be conspicuously posted at the entrance to rooms or on cabinets comtaining compresses gases. • “NO SMOKING” signs shall be posted at entrance to and in areas containing flammable compressed gas cylinders, piping and equipment. • The signs should indicate the presence of compressed-gas-associated hazards by including the relevant pictogram(s). • Specific signage may be needed regarding specific gases and emergency call procedures. • Laboratory personnel should not accept incoming compressed gas cylinders if the manufacturer’s label is missing, damaged, illegible or incomplete. • Laboratory personnel should not deface manufacturer’s labels from the compressed gas cylinder or remove or alter any tags, stencil marks or other markings used by the supplier for identification of the cylinder contents. • Empty compressed gas cylinders must be marked as “EMPTY” and stored separately from in-use compressed gas cylinders. • Laboratory door signs for Columbia University can be downloaded and printed from the EH&S website at the following link: https://research.columbia.edu/content/laboratory-door-signs | [5 empty] | N/A |  | N/A
[7 empty] | N/A |  | N/A
Storage | • Limit access to storage area to authorized personnel • Store cylinders in a well-protected, well-ventilated, dry location, at least 20 (6.1m) feet from highly combustible materials such as oil or excelsior, and never in unventilated enclosures such as lockers or cupboards. • Gas rooms, gas cabinets and exhausted enclosures shall be equipped with a sprinkler system and ventilated • Keep cylinders vertical. • Secure with straps or chains connected to a wall bracket or other fixed surface, or by use of a cylinder stand to prevent falling. Restraints must be fastened on the upper half of the cylinder above the center of gravity. • Full cylinders should be stored separate from empty cylinders. • Do not let indoor temperature exceed 125°F (51.7°C). • Place safety caps on cylinders when not in use. • Store incompatable gases away from each other. • Cylinders shall not be kept in unventilated enclosures such as lockers and cupboards. • Do not place cylinders where they may become a part of an electric circuit, and do not secure them to electrical and plumbing conduits. | • Do not store near oxidizing agents such as Oxygen cylinders. Unless they are well seperated, there should be a noncombustible partition of atleast 5ft (1.5m) high with a fire resistive rating of one-half hour between the two. •Store away from any readily combustible materials such as paper or combustible fiber. • Bond and ground all cylinders, lines and equipment used with flammable compressed gases. • Flammable gasses in pre-existing laboratories: 9.24 ft3 for 500 ft2 of lab space plus 1.54 ft3 per each additional 100 ft2 up to 15.4 ft3 for labs > 900 ft2. | • Reactives gases must not be stored with other gases. | • Store oxidizing gases in a well-ventilated area away from incompatibles. These incompatibles include: Flammable and combustible liquids/materials. • Greasy and oily materials should never be stored near oxygen cylinders. • Never lubricate valves, regulators, gauges or other connections with combustible materials such as oil or handle these parts with oily hands or gloves. | • Can only be stored in a fume hood, gas cabinet or room. • Gas cabinets and exhausted enclosures must not be the only source of ventilation in a room where toxic, highly toxic or reactive gases are stored. | • Can only be stored in a fume hood, gas cabinet or room. • Gas cabinets and exhausted enclosures must not be the only source of ventilation in a room where toxic, highly toxic or reactive gases are stored. | • Provide adequate ventilation for inert gases in storage. • Laboratory personnel are required to continuously monitor the level of oxygen in the area where cryogenic gases are used or dispensed in quantities >60 gallons. The alarm shall actuate when oxygen concentration drops below 19.5% per FDNY NYC Fire Code Section 3205.4.1.1.1. | • Cylinders must be stored in continuously ventilated and fire suppressive gas cabinets equipped with a sprinkler system. • Lecture bottles can be stored in ventilated storage cabinets or fume hoods, away from other combustible and flammable materials. • Silane: Avoid contact with air at all times. Should be stored under positive preessure. Handle silane in a well-ventilated area while avoiding the presence of combustible materials. Do not use silane in conjunction with heavy-metal halides or free halogens, with which it will react violently. | • Laboratory personnel are required to continuously monitor the level of oxygen in the area where cryogenic gases are used or dispensed in quantities >60 gallons. The alarm shall actuate when oxygen concentration drops below 19.5% per FDNY NYC Fire Code Section 3205.4.1.1.1
Handling/Moving Cylinders | • Wear adequate PPE for the hazards involved in moving compressed gas cylinders. • Use hand trucks along with chaining to secure the cylinder while moving it. • Protective valve caps must be secured when moving cylinders. • Never attempt to transfer gas from one cylinder to another, to refill cylinders or to mix any other gas to the cylinder. • Never use cylinders as rollers or support or for any other purpose other than storing. • Cylinders must not be transported laying horizontally on the hand truck with the valve oherhanging in a position to collide with stationary objects. • Cylinders should never be dragged from place to place, or dropped and slid on the floor. • Laboratory personnel shall never use ropes, chains or slings to lift or suspend compressed gas cylinders • Do not lift or move the cylinder by the cap. • Never attempt to puncture or remove the cylinder head from any cylinders, even if they "appear" empty. • All movement of cylinders between campuses or to or from a destination off campus must be done using a University approved vendor and by a trained professional. | N/A | N/A | N/A | N/A | N/A | N/A | • Spark-resistant tools shall be used when attaching components to the pyrophoric compressed gas cylinders. Silane: Handle silane in a well-ventilated area while avoiding the presence of combustible materials. | N/A
Ventilation | • Exhausted enclosure (fume hood) storage is required for: lecture bottles with an NFPA health hazard rating of 3 or 4, with a health hazard rating of 2 and no physiological warning properties or containing pyrophoric gasses • Gas cabinet storage is required for cylinders larger than lecture bottles with a health hazard rating of 3 or 4 or with an NFPA health hazard rating of 2 and no physiological warning properties. • Gas Cabinets Supply and exhaust ducts should be enclosed in a 1-hour fire-resistance-rated shaft enclousure. • Average velocity: At the face of access ports/windows- not less than 200 feet per minute. At any point of access poart/windows- not less than 150 feet per minute. Gas cabinets shall be connected to an exhaust system. Gas cabinets should not be the sole means of an exhaust system. Maximum number of cylinders in the gas-cabinets must not exceed three , with an exception of cylinders less than 1 pound each are allowed to have 100 cylinders. | • Must be carefully handled in a certified chemical fume hood. | • Chlorine: Moisture should be avoided as chlorine can corrode steel. Chlorine forms plugs in the valve when exposed to moisture and may "appear" to be empty. | N/A | • Must be carefully handled in a certified chemical fume hood. | Gases that have an NFPA Health Hazard Rating of 3 or 4 (e.g., hydrogen sulfide) must be stored in a continuously mechanically ventilated gas cabinet. • Gases that have an NFPA Health Hazard Rating of 2 without warning properties (e.g., carbon monoxide) must be stored in a continuously mechanically ventilated gas cabinet. • Must be carefully handled in a certified chemical fume hood. | N/A | • Cylinders larger than lecture bottles containing pyrophoric gas must be kept in a gas cabinet equipped with a sprinkler system. | • The space must be ventilated in a manner that captures any vapor at the point of generation.
Tubing/piping | • Cross-threading or force fitting regulators on tubing, or lubricating connections to facilitate attachment to a compressed gas cylinder is unsafe and strictly prohibited. Note: Please consult with the Compressed gas supplier/Vendor prior to its use and installation. | • For Acetylene- Only steel or wrought-iron pipes must be used for the piping system. Cast iron and copper fittings are not permitted. | • Chlorine: Keep equipment free of moisture to prevent formation of hypochloric and hypoclorus acid. | N/A | N/A | N/A | N/A | Silane: • Piping and equipment that come in cantact with silane gas must be of steel or stainless steel. • Heavy metal halide and heavy metal containing materials must be avoided as it can react violently or explosively with these compounds. • Silane should never be purged through a vacuum pump. | N/A
Regulators/Valves | • Before installing a regulator, laboratory personnel must ensure that it has been approved by the manufacturer for use with their specific gas. This is because different types of regulators may be required for different types of gases. • Never cross-thread or force fit regulators on tubing, or lubricate connections to facilitate attachment to a compressed gas cylinder. • Regulators must not be tampered with, altered or manually repaired by laboratory personnel. • Regulators must be inspected regularly by laboratory personnel to ensure the absence of cracks or evidence of damage. In case of damages, such as worn threading, damaged outlet/inlet, manufacturers should be contacted. • All regulators must be removed before transporting or relocating compressed gas cylinders. • Proper PPE such as safety goggles/glasses must be worn while working on regulators. • Valves shall never be opened without a regulator attached. Always open cylinder valves slowly. •Never tamper with the pressure-relief device in valve or cylinders. • Do not obstruct any pressure-relief device. Dirt, paint, corrosion, or other materials prevent pressure-relief devices from functioning properly. | • Cylinder valves on flammable gases have a left hand thread to attach the regulator, they are tightened by turning the nut counterclockwise. This is to distinguish them from non-flammable gases. • Regulators for flammable gases are left hand threaded and have a notch cut out of faces on the securing nut to distinguish them from non-flammable gas regulators. • Regulators are designed to be fitted directly to the cylinder valve. No other fittings, connections or lubricants shall be used to connect a regulator to a gas cylinder valve. | N/A | N/A | N/A | • Toxic gases such as PIH's do not have pressure relief devices. Do not expose them to high temperatures or attempt to tamper with the valves. | N/A | N/A | N/A
Leak Testing | • Compressed gas cylinders should be checked for potential leaks as part of a regular safety inspection. • Every time a new connection is made, additional equipment is attached to the valve, a regulator is added or replaced, or any alteration to the installation takes place a leak check should be performed. • Leak testing should be done before using the compressed gas cylinder for the first time or whenever a user suspects a leak (e.g. low pressure may be an indication of a leak). • To check for leaks, laboratory personnel may use a manufacturer or supplier’s recommendation for a leak testing solution or a dilute soap solution. However, soap can render the surface of the cylinder slippery and make handling and/or use, difficult or unsafe. EH&S recommends the use of specialized leak detection products (e.g. Snoop). | N/A | N/A | N/A |  | • If using toxic gases, the use of additional leak detection methods is recommended (e.g. monitor devices or gas detectors). | N/A | • Silane: Evacuate and thoroughly pressure check all systems, preferably with helium, for leaks at pressures two to three times the anticipated working pressure. Use an alternate vacuum and inert gas purge of the system to purge all air out of the system after it has been leak checked or opened for any reason. | N/A
Monitoring/Alarms | • A gas detection system must be used to detect the presence of highly toxic or toxic gas at or below the permissible exposure limit (PEL) or ceiling limit of the gas for which detection is provided. • The detection system shall alarm when the presence of gas reaches or exceeds 25% of the LEL or at one-half of the IDLH concentration per IFC 5303.16.10. | • Flammable gas detection and alarm systems are required in areas where flammable gas distribution piping operates at levels above 15 pounds per square inch FDNY NYC Fire Code Section 908.9.1. | N/A | N/A | N/A | • Gas detection systems are required in laboratories using: - 20 scf/ 4 lb or more of “highly toxic” gas or - 810 scf/ 150 lb or more of “toxic” gas according to NFPA 55. | • An oxygen monitoring device shall be installed by EH&S in any indoor location where compressed gases are stored and/or dispensed in manner that could create the potential for the displacement of oxygen. | N/A | • An oxygen sensor equipped with an audible alarm shall be provided by EH&S in dispensing areas to continuously monitor the level of oxygen in the area.
Maximum Quantity Allowed | • 25 lecture bottles per lab – lecture bottles are small compressed gas containers up to a size of 2” by 13” [C-14 pg 7, NFPA 45 11.1.6.6]. | • Storage capacity: 2500 cubic feet (70 cubic meter). • Flammable Gases: 12 ft3 for 500 ft2 of lab space; plus 2.4 ft3 per each additional 100 ft2 • Liquefied flammable gases: 2.4 ft3 for 500 ft2 of lab space; plus 0.36 ft3 per each additional 100 ft2. • Amount of gas allowed per ft2 of lab space- 0.012 ft3 • Flammable gasses in pre-existing laboratories: 9.24 ft3 for 500 ft2 of lab space plus 1.54 ft3 per each additional 100 ft2 up to 15.4 ft3 for labs > 900 ft2 [C-14, pg 1, 23, 24; FC 2706]. | N/A | • 12 ft3 for 500 ft2 of lab space; plus 2.4 ft3 per each additional 100 ft2 | N/A | • Health Hazard 3 or 4 Gasses: 0.3 ft3 for 500 ft2 of lab space; plus 0.06 ft3 per each additional 100 ft2. | N/A | N/A | N/A
NFPA Diamond
Note on A8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: I'm not sure we need a transport column as we do not want people transporting cylinders. If by transport you mean around the lab or within the building, then maybe we should clarify that defintion for the lab people. But, realistically, all cylinders should be safely transported as Vincent already wrote in the manual so I'm not sure it warrants a column at all in this table... Reply: Storage in the lab? Or storage in a ventilated cabinet? Maybe make a list of what we mean here: ventilated cabinet required or differentate it from the max. amount stored in the lab per FDNY?
Note on A9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For ventilation, I'm thinking what restrictions they may have or do you mean where they should be allowed to use certain gases?
Note on A10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: I think the language here should be more clear. For example, recommended tubing and piping types. We wouldn't want them to use copper for acetylene operations etc.
Note on A14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Let's clarify that we mean FDNY maximum quantity allowed or if some other restrictive agency/regulation

## Howie's reference
Anyway, the only regs we are aware of with regard to cylinder storage which has been an issue for us in the past is the storage of propane gas cylinders which are occasionally used in labs.
We have had the NYS Dept of Homeland Security, Fire Prevention Bureau conduct annual inspections here for the past 6 or 7 years.
During the inspections they have come across situations where a propane cylinder was in a lab; typically these are used by lab persons for some minor heating of glassware on an intermittent basis.
According to the Fire Prevention inspection, Chapter 27 in the NYS Fire Code, propane may be permitted for usage and temporary storage in work locations (other than Classrooms). Additionally, there is language there to describe the quantity of stored gas in cylinders, generally not to exceed 12lbs of water equivalent for Educational occupancies. (They claim that our situation is actually a Business occupancy for the labs).
In any event, what we now do is have the propane cylinders stored on the Comer Loading Dock in the cylinder storage area when not in use; This satisfied their concerns as a control area is in line with the more restrictive and safer practice.

## Sheet4
Ammonia (NH3)
Dichlorosilane (SiH2Cl2)
Difluoromethane (CH2F2)
Octofluorocyclobutane (C4F8
Acetylene
Arsine
Boron Trichloride (BCl3)
Butane
Carbon dioxide
Carbon monoxide
Chlorine
Chlorine trifluoride
disilane
Ethane
Ethylene oxide
Fluorine
Helium
Hydrogen
Hydrogen chloride
Hydrogen fluoride
Hydrogen sulfide
Krypton
Methane
Nitric oxide
Nitrogen
Oxygen
Phosgene
Phosphine
Phosphine
Propane
silane
Sulfur dioxide
Sulphur hexafluoride
Trimethyl boran
Xenon